Task Force Report on Conversion of Units of Power to Boiler Horsepower

Maryland State Board of Stationary Engineers

12/12/2007

Prepared by Karl Kraft, Chief Boiler Inspector

Definitions

1. Horsepower is a measure of the rate at which work is done.

2. Within the scope of this Statute and Regulations, "horsepower" (abbreviated "hp") means

"boiler horsepower" (abbreviated "hp-b").

3. To convert units of power to boiler horsepower, use the following equations:

To get boiler horsepower, multiply    	by

1. [lb (mass) of steam]/hr                	0.029

2. Btu/hr                             		0.0000299

3. Square Feet of Heating Surface           0.2

(Note: This factor can vary

significantly. The conversion

shall be supported by design

documentation.)

4. Watts (W)                           		0.000102

5. Electric Horsepower (hp-elect)         	0.076

6. Mechanical horsepower (hp-mech)     0.076

7. Tons (of cooling capacity)             	0.358

Derivation of Conversion Factors:

Conversion Factor   	=            Unity   x                      Unity

1.  0.029                 hp-b___   	=                1      x     1                       hp-b______

[lb (mass) of steam]/hr                                         34.5  [lb (mass) of steam]/hr

2.  0.0000299         hp-b__   	=                1      x     1                      hp-b______

Btu/hr                            		          33,475      Btu/hr

3.  0.2                    hp-b____   	=                1      x     1                       hp-b______

Sq ft of Heating Surface                                         5   Sq ft of Heating Surface

(Note: This factor can vary

significantly. The conversion

shall be supported by design

documentation.)

4.  0.000102           hp-b   	=                    1              x    1               hp-b

watt                            	                  9810           W

5.  0.076                 hp-b   	=   	746         W       x    1              hp-b

hp-elect             		    hp-elect              9810           W

6.  0.076                 hp-b   	=   	746          W       x    1              hp-b

hp-mech              		    hp-mech             9810           W

7.  0.358                 hp-b   	=   	12,000  Btu/hr   x    1            hp-b_

Ton                  		Ton            33,475   Btu/hr